STEAM DRUM

The steam drum is a cylinder located at the top of the boiler. It runs lengthwise (fig. 4-1) from the front to the back of the boiler.  The steam drum provides a space for the saturated steam generated in the tubes and for the separation of moisture from the steam. (Remember, saturated steam is steam that has not been heated above the temperature of the water from which it was generated).  The  steam  drum  also  serves  as  a storage space for boiler water, which is distributed from  the  steam  drum  to  the  downcomer  tubes. During normal operation, the steam drum is kept about half full of water. The steam drum either contains or is connected to many of the important controls and fittings required for the operation of the boiler. At the bottom right side of the boiler you will find the water drum, and on the bottom left side is the sidewall header (fig. below). Notice the header is smaller than the water drum. Most boilers have more than one header. They are identified by their location.  For example,  a  header  at  the  back  of the boiler is called a rear wall header. A header on a screen wall is called a screen wall header.

WATER DRUM

The water drum is larger than the header, but both are smaller than the steam drum. The water drum equalizes the distribution of water to the generating tubes. Both the water drum and the header collect the deposits of loose scale and other solid matter present in the boiler water. Both the drum and the header have bottom blowdown valves.  When these valves are opened, some of the water is forced out of the drum or header and carries any loose particles with it. DO NOT OPEN THE BOTTOM BLOWDOWN VALVES ON A STEAMING BOILER. Opening these valves will interrupt the circulation of the steam cycle. DOWNCOMER TUBES At each end of the steam drum are a number of large tubes (fig. below) that lead to the water drum and side wall header. These tubes are the downcomers through which water flows down- ward from the steam drum to the water drum and the header.  The downcomers range in diameter from 3 to 8 inches (76 mm to 200 mm).

GENERATING TUBES

Many tubes link the steam drum to the water   drum   and   to   the   header.   The tubes that lead from the water drum to the steam drum   are   the   generating tubes (fig.   4-4). They are   arranged   in   the   furnace   so   the gases and the heat of combustion can flow around them.  The  large  arrows  in  figure  4-4 show  the direction  of  flow  of  the  combustion gases. The generating tubes are made of steel that is strong enough to withstand the high pressures and   temperatures   within   the boiler.   In   most boilers  these  tubes  are  usually  1  to  2  inches in  diameter,  but some  may  be  3  inches.  These small tubes present a large surface area to absorb furnace heat.  A  2-inch  tube  has  twice the  surface  area  of  a  1-inch  tube  but four times  the  volume.  A 3-inch tube has three times the surface area of a 1-inch tube but nine times the volume. The smaller the diameter of the tube, the higher is the ratio of absorption surface to the volume of water.

Normally,  only  one  row  of  tubes  leads from  the  steam  drum  to  the  sidewall header. These are the sidewall (water wall) tubes. Their function  is  to  cool  and protect  the  side  wall  of the  furnace. So far, we have assembled the drums, header, downcomers, and generating tubes. Before going any further with the assembly, let us trace the path of the water through the boiler. As the water is heated, it becomes less dense, and steam is formed in the tubes. The water in the steam drum is much cooler than the steam and has greater density. As the hotter water and steam rise through  the  generating  tubes,  the  cooler  more dense  water  drops  through  the downcomers  to  the water drum and headers. The arrows in figure below show the circulation path of the water as it leaves the steam drum and returns to the steam drum as steam.  Notice  that  the  circulation  is  an accelerated  type.  This is indicated by the inclination of the tubes. The tubes shown are almost vertical. The greater the incline, the greater the acceleration.

So  far,  we  have  learned  how  the  steam  is formed  in  a  boiler.  Next,  let’s  find out  what happens  to  the  steam  once  it  returns  to  the  steam drum  from  the generating  tubes.

INTERNAL FITTINGS

Components   of   the   steam   drum   area   are known as INTERNAL FITTINGS. The  internal fittings  we  will  discuss  are  the  feedwater distribution,  the  chemical injection,  and  the  steam and water separator. This equipment is used to direct  the flow  of  steam  and  water  within  the steam  drum  and  the  desuperheaters,  which are located  either  in  the  steam  drum  or  the  water drum. We will also discuss the economizer in this section.  This  component  is  not  considered  an internal  fitting, but  its  role  is  important  to  the function  of  the  steam  drum. The   design drum’s internal and arrangement of steam fittings will vary somewhat from one type of boiler to another and from one boiler manufacturer to another.  Figure 4-6 shows the arrangement of the steam drum internal fittings in a single-furnace boiler.

- The feedwater   pipe   receives   feedwater from  the  economizer  and  distributes  it throughout the  length  of  the  steam  drum.

- The  chemical  feed  pipe  is  used  to inject chemicals into the boiler to maintain the proper pH  and  phosphate  balance  in the  boiler  water.

- The surface blow pipe is used to remove suspended solid matter that floats on top of the water and to lower the steam drum water level, when necessary.

- The surface blow pipe is also used to blow water out to lower the chemical level in the boiler when it becomes too high.

- The dry pipe is used to direct the steam to the steam drum outlet nozzle after it leaves the scrubbers.

- The vortex eliminators are used to reduce the swirling motion of the water as it enters the downcomers. It also prevents the steam from being drawn from the upper portion of the drum into the downcomer.

- The baffle plates are used to direct the steam to the steam separators.

- The   cyclone   steam   separators   remove moisture from the steam.

- This is accomplished by the steam spinning or changing direction.

- The water drains back into the steam drum while the steam continues upward through a screen and scrubber that removes still more moisture.

After the steam leaves the scrubbers, it goes to the dry pipe (fig. 4-6). From there it leaves the steam   drum   through   the   steam   drum   outlet. Figure 4-7, view A, shows the steam going to the inlet   header   of   the   superheater   and   passing through  the  U-shaped  tubes  of  the  superheater  to the next header (fig. 4-7, view B). This header is called the first pass or intermediate header. Steam may  pass through  the  U-shaped  tubes  several times  before  passing  to  the  outlet  header. Each time the steam goes from one header to the next header it is called a pass. The number of passes the  steam  makes  in  a  superheater  varies  with different boilers and the degree of superheat that is  required  for  a  particular  ship.

As  the  steam  passes  through  the  super- heater tubes, it is heated by the hot gases from combustion,  which  flow  around  the  tubes. In some boilers, the superheater headers are installed parallel with the water drum; and the tubes are installed vertically (fig. 4-8). These are called vertical superheaters. Another boiler internal fitting is the desuperheater. It maybe located either in the steam drum or in the water drum. All the steam generated in a single-furnace boiler is led through the superheater.   However,   since   some   auxiliary machinery is not designed for superheated steam, the steam must be cooled down. This is done with a desuperheater.  The desuperheater gets steam from the superheater outlet, as shown in figure 4-9.  The desuperheater is submerged in water either in the steam drum or in the water drum. As the steam passes through the desuperheater, it is cooled for use in the auxiliary steam systems.

Internal Desuperheater [also called Attemperator]