# Boiler water tests

### Corrosion and tube failure caused by water chemistry

Recommended ranges (Co-ordinated phosphate treatment for w/t boiler)

| pH | - 9.6 to 10.3 |
| --- | --- |
| PO4 | - 4 to 20 ppm |
| N2H4 | - 0.01 to 0.03 ppm |
| TDS | - < 150 ppm |
| Cond pH | - 8.6 to 9.0 |
| Cl | - 20 ppm |
| O2 | - 10 ppb |
| Si | - 10 ppb |

Chlorides

  - Measure 100ml of sample water into a casserole

  - Add 10 drops phenol pthalein (RE 106)

  - Neutralize with sulphuric acid

  - Add 10 drops of Potassium Chromate

  - Titrate Silver Nitrate untill sample just turns brick red

  - ppm as CaCO3= (ml x 10) ppm

TDS

  - Measure 100ml of sample water into a casserole

  - Add 10 drops of phenolpthalein

  - Neutralise with TDS reagent (acetic acid)

  - Temperature compensate then read off scale in ppm.

Phosphates

  - Fill one 10 ml tube with distilled water

  - Fill one 10 ml tube with boiler water tests.

  - Add 0.5 ml sulphuric acid (RE 131) to each 
Add 0.5 ml Ammonium Molybdnate (RE130) to each 
Add 0.5 ml Aminonapthol Sulfonic acid (RE 132) to each 
Stir well between each addition

  - Wait 3 minutes for calorimetric compaison

Alternately Vanado-molybdnate test

  - Place 5 ml boiler water in 10 ml tube

  - Place 5 ml distilled water in other 10 ml tube

  - Top both to 10 ml with Vanado-molybdnate reagent

  - Place in colour comparator and compare after 5 mins

Hydrazine

  - Add 9ml distilled water to one tube

  - Add 9 ml boiler test water to anouther

  - Add 1 ml hydrazine reagent to each

  - Use colour comparator

Alkalinity Phenolpthalein

  - 100 ml filtered water

  - Add 1 ml phenolpthalein

  - If pH >8.4 Solution turns pink

  - Add H2SO4 untill pink disapears

  - Ml 0.02N H2SO4 x 10 = ALk in CaCO3 ppm

  - Measures hydroxides and carbonates in sample, bi-carbonates do not show up so sample should not be allowed to be exposed to the air for too long

Alkalinity Methyl orange

Bi carbonates do not show up in the phenolpthalein sample as they have a pH < 8.4. Bi carbonates can not occur in boiler but if suspected in raw feed then the following test.

  - Take phenolpthalein sample, add 1 ml methyl orange

  - If yellow, bi carbonates are present

  - Add H2SO4 until red

  - Total 0.02N H2SO4 x 10 = Total Alk in CaCO3

pH

  - 100 ml unfiltered sealed water poured into two 50 ml glass stoppered test tubes

  - Add 0.2 ml pH indicator to one ( pH indicator vary's according to required measuring range)

  - Use colour comparator

  - Due to difficulty of excluding air, electronic pH meter preferred

Sulphite reserve

  - Exclude air at all stages

  - 100 ml unfiltered water

  - Add 4 ml H2SO4 + 1 ml starch

  - Add potassium iodate-iodide until blue colour

  - ml Iodate-Iodide sol x 806 / ml of sample = SO3 reserve in ppm

Ammonia in feed

  - Only necessary where N2H4 used in blr

  - Pour condensate sample into two 50 ml colour comparator tubes

  - Add 2 ml Nessler reagent to one

  - Wait 10 mins

  - Use colour comparator