SLIDING FEET CONFIGURATION

Sliding Feet

Since the boiler expands and contracts as it heats up and cools down, sliding feet are installed to allow the boiler to move easily. The feet are located below the boiler, usually under the front end of the sidewall header and water drum. There is a greased phosphor-bronze friction plate on which these feet will move. The planned maintenance system (PMS) requires lubricating the sliding feet every month. Some newer ships have permalube sliding feet which never require lubrication. Failure of the sliding feet to move can cause cracks in the air casing and can cause header handhole plug leaks. Movement indicators are installed on the sliding feet which have to be checked prior to light off, during warm up, and after the boiler is on line to ensure positive movement of the sliding feet. Each time sliding feet are checked the results should be logged in the fireroom operating log.