Conditions for effective combustion

To understand the basics of efficient boiler operation, the combustion process must be understood.

Stable combustion conditions requires the right amounts of fuels and oxygen. The combustion products are heat energy, carbon dioxide, water vapor, nitrogen, and other gases (excluding oxygen). In theory there is a specific amount of oxygen needed to completely burn a given amount of fuel. In practice, burning conditions are never ideal.

Therefore, more air than ideal must be supplied to burn all fuel completely. The amount of air more than the theoretical requirement is referred to as excess air.

Power plant boilers normally run about 10 to 20 percent excess air. Natural gas-fired boilers may run as low as 5 percent excess air. Pulverized coal-fired boilers may run with 20 percent excess air. Gas turbines run very lean with up to 300 percent excess air.

Typical values of excess air for some common fuels are shown in the table below:

| Fuel | Excess of Air (%) |
| --- | --- |
| Anthracite | 40 |
| Coke oven gas | 5 - 10 |
| Natural Gas | 5 - 10 |
| Coal, pulverized | 15 - 20 |
| Coal, stoker | 20 - 30 |
| Oil (No. 2 and No. 6) | 10 to 20 |
| Semi anthracite, hand firing | 70 to 100 |
| Semi anthracite, with stoker | 40 to 70 |
| Semi anthracite, with traveling grate | 30 to 60 |

To determine the excess air at which the combustion system will operate we have to start with the stoichiometric air-fuel ratio, known as the perfect, correct or ideal fuel ratio, the stoichiometric combustion. During stoichiometric combustion there are a chemically correct mixing proportion between the air and the fuel. During the stoichiometric combustion process no fuel or air are left over.

Process heating equipment almost never run stoichiometric. Even so-called "on-ratio" combustion, used in boilers and high temperature process furnaces, incorporates a modest amount of excess air, 10 to 20% more than needed to burn the fuel completely.

If insufficient amount of air is supplied to the burner, unburned fuel, soot, smoke, and carbon monoxide are exhausted from the boiler. The results is heat transfer surface fouling, pollution, lower combustion efficiency, flame instability and a potential for explosion. To avoid inefficient and unsafe conditions, boilers normally operate at an excess air level. This excess air level also provides protection from insufficient oxygen conditions caused by variations in fuel composition and "operating slops" in the fuel-air control system.

Stoichiometric combustion

Stoichiometric or Theoretical Combustion is the ideal combustion process during which a fuel is burned completely. A complete combustion is a process which burns all the carbon (C) to (CO2), all hydrogen (H) to (H2O) and all sulphur (S) to (SO2). If there are unburned components in the exhaust gas such as C, H2, CO the combustion process is uncompleted.

The combustion process can be expressed as:

[C + H (fuel)] + [O2 + N2 (Air)] -> (Combustion Process) -> [CO2 + H2O + N2 (Heat)]

where

C = Carbon

H = Hydrogen

O = Oxygen

N = Nitrogen

To determine the percent excess air or excess fuel at which a combustion system operates, you have to start with the stoichiometric air-fuel ratio. Also known as the perfect, correct or ideal fuel ratio, the stoichiometric ratio is the chemically correct mixing proportion. When burned, it consumes all the fuel and air without any excess of either left over.

Process heating equipment is rarely run that way, however. Even so-called "on-ratio" combustion, used in boilers and high temperature process furnaces, usually incorporates a modest amount of excess air -- about 10 to 20% beyond what is needed to burn the fuel completely.

If insufficient amount of air is supplied to the burner, unburned fuel, soot, smoke, and carbon monoxide exhausts from the boiler. This results in heat transfer surface fouling, pollution, lower combustion efficiency, flame instability and a potential for explosion. To avoid inefficient and unsafe conditions, boilers normally operate at an excess air level. This excess air level also provides protection from insufficient oxygen conditions caused by variations in fuel composition and "operating slops" in the fuel-air control system. Typical optimum values of excess air levels are shown here for various fuels.

- if the air content is higher than stoichiometric, the mixture is said to be fuel-lean

- if the air content is less, the mixture is fuel-rich

- Excess air of different fuels

### Example - Stoichiometric Combustion of Methane - CH4

The most common oxidizer is air. The chemical equation for stoichiometric combustion of methane - CH4 - with air can be expressed as

CH4 + 2(O2 + 3.76N2) -> CO2 + 2H2O + 7.52N2

If more air is supplied, not all will be involved in the reaction. Additional air is termed excess air, but the term theoretical air may also be used. 200% theoretical air is 100% excess air.

The chemical equation for methane burned with 25% excess air can be expressed as

CH4 + 1.25 x 2(O2 + 3.76 N2) -> CO2 + 2H2O + 0.5O2 + 9.4N2

### Excess Air and O2 and CO2 in Flue Gas

Aproximate values for CO2 and O2 in the flue gas as result of excess air are estimated in the table below:

| Excess Air % | Carbon Dioxide - CO2 - in Flue Gas (% volume) |  |  |  |  | Oxygen in Flue Gas for all fuels (% volume) |
| --- | --- | --- | --- | --- | --- | --- |
|  | Natural Gas | Propane Butane | Fuel Oil | Bituminous Coal | Anthracite Coal |  |
| 0 | 12 | 14 | 15.5 | 18 | 20 | 0 |
| 20 | 10.5 | 12 | 13.5 | 15.5 | 16.5 | 3 |
| 40 | 9 | 10 | 12 | 13.5 | 14 | 5 |
| 60 | 8 | 9 | 10 | 12 | 12.5 | 7.5 |
| 80 | 7 | 8 | 9 | 11 | 11.5 | 9 |
| 100 | 6 | 6 | 8 | 9.5 | 10 | 10 |

Typical combustion process efficiencies can be summarized as

- home fireplace: 10 - 40 %

- space heater: 50 - 80 %

- gas boiler: 70 - 80 %

- residential gas furnace with low efficiency atmospheric burner: 70 - 80 %

- oil burner heating system: 70 - 85 %

- gas powered boiler: 75 - 85 %

- high efficiency gas or oil condensing furnace: 85 - 95 %

NOx concerns

Emission of Nitrogen Oxides - NOx - when burning some common fuels can be approximated from the table below:

| Fuel | Emission of NOx (g/kg fuel) |
| --- | --- |
| Oil | 3.0 |
| Kerosene | 3.0 |
| Coal | 4.5 |
| Propane | 2.3 |
| Gasoline | 27.0 |
| Hydrogen | 0 |
| Natural Gas | 1.0 |
| Butane | 2.3 |
| Wood | 0.7 |

NOx emissions contribute to eutrophication, acidification and the formation of ground-level ozone.

Performance/Costs: An often-stated rule of thumb is that boiler efficiency can be increased by 1% for each 15% reduction in excess air or 40°F reduction in stack gas temperature. An annual fuel savings of 5% is often obtained with tighter excess air control. Table 2 relates stack readings to boiler performance, clearly demonstrating the efficiency improvements available through control of excess air.